## Sheet3
性能表 Performance table 表1
风机型号 | 转速 | 理论流量 | 各排气压力下的进口流量Qs(m3/min),所需轴功率La(kW)及所配电机功率Po(kW) | [29 empty] | 电机
| Speed | Thero volume | Inlet volume Qs(m3/min) shaft power required La (kW) and motor power Po(kW) at each discharge pressure | [29 empty] | 极数
Type | r/min | m3/min | 9.8kPa |  |  | 19.6kPa |  |  | 29.4kPa |  |  | 39.2kPa |  |  | 49.0kPa |  |  | 58.8kPa |  |  | 68.6kPa |  |  | 78.4kPa |  |  | 88.2kPa |  |  | 98.0kPa |  |  | Motor pole
| n | Qth | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | P
JAS-80 | 1150 | 4.65 | 3.36 | 1.3 | 2.2 | 3.01 | 2.1 | 3 | 2.71 | 2.8 | 4 | 2.46 | 3.5 | 5.5 | 2.21 | 4.3 | 5.5 | 2.01 | 5 | 7.5 | [12 empty] | 4
| 1450 | 5.88 | 4.59 | 1.6 | 2.2 | 4.24 | 2.6 | 4 | 3.94 | 3.6 | 5.5 | 3.69 | 4.5 | 5.5 | 3.44 | 5.5 | 7.5 | 3.24 | 6.5 | 7.5 | 3.09 | 7.5 | 11 | [9 empty] | 4
| 1750 | 7.09 | 5.8 | 2 | 3 | 5.45 | 3.1 | 4 | 5.15 | 4.3 | 5.5 | 4.9 | 5.4 | 7.5 | 4.65 | 6.5 | 7.5 | 4.45 | 7.7 | 11 | 4.3 | 8.9 | 11 | 4.15 | 10 | 15 | [6 empty] | 4
| 2000 | 8.01 | 6.81 | 2.3 | 3 | 6.46 | 3.6 | 5.5 | 6.16 | 4.9 | 7.5 | 5.91 | 6.2 | 7.5 | 5.66 | 7.5 | 11 | 5.46 | 8.8 | 11 | 5.31 | 10.1 | 15 | 5.16 | 11.4 | 15 | [6 empty] | 2
| 2500 | 10.1 | 8.79 | 2.9 | 4 | 8.5 | 4.6 | 5.5 | 8.2 | 6.2 | 7.5 | 7.95 | 7.9 | 11 | 7.7 | 9.5 | 11 | 7.5 | 11.2 | 15 | 7.35 | 12.9 | 15 | 7.2 | 14.5 | 18.5 | [6 empty] | 2
JAS-100 | 1150 | 6.57 | 5.11 | 1.8 | 3 | 4.72 | 2.9 | 4 | 4.38 | 3.9 | 5.5 | 4.08 | 5 | 7.5 | 3.81 | 6.1 | 7.5 | 3.58 | 7.2 | 11 | 3.38 | 8.3 | 11 | [9 empty] | 4
| 1450 | 8.29 | 6.84 | 2.3 | 3 | 6.45 | 3.6 | 5.5 | 6.11 | 4.9 | 7.5 | 5.81 | 6.3 | 7.5 | 5.54 | 7.6 | 11 | 5.31 | 9 | 11 | 5.11 | 10.3 | 15 | [9 empty] | 4
| 1750 | 10 | 8.56 | 2.7 | 4 | 8.17 | 4.3 | 5.5 | 7.83 | 5.9 | 7.5 | 7.53 | 7.4 | 11 | 7.26 | 9 | 11 | 7.03 | 10.7 | 15 | 6.83 | 12.3 | 15 | [9 empty] | 4
| 2000 | 11.4 | 9.99 | 3 | 4 | 9.6 | 4.8 | 7.5 | 9.26 | 6.7 | 11 | 8.96 | 8.6 | 11 | 8.69 | 10.5 | 15 | 8.46 | 12.4 | 15 | 8.26 | 14.3 | 18.5 | [9 empty] | 2
| 2500 | 14.3 | 12.85 | 3.9 | 5.5 | 12.45 | 6.2 | 7.5 | 12.1 | 8.5 | 11 | 11.85 | 10.8 | 15 | 11.55 | 13.1 | 18.5 | 11.35 | 15.4 | 18.5 | [12 empty] | 2
JAS-125 | 970Δ | 11.5 | 8.85 | 2.6 | 4 | 8.25 | 4.5 | 7.5 | 7.87 | 6.4 | 7.5 | 7.42 | 8.3 | 11 | 7.07 | 10.2 | 15 | 6.72 | 12.1 | 15 | 6.39 | 14 | 18.5 | 6.12 | 16 | 18.5 | [6 empty] | 6
| 1150 | 13.7 | 11.53 | 3.1 | 5.5 | 10.93 | 5.3 | 7.5 | 10.42 | 7.6 | 11 | 9.97 | 9.9 | 15 | 9.62 | 12.2 | 15 | 9.27 | 14.4 | 18.5 | 8.97 | 16.7 | 22 | 8.67 | 19 | 30 | 8.42 | 21.3 | 30 |  |  |  | 4
| 1450Δ | 17.2 | 14.67 | 4 | 5.5 | 14.07 | 6.8 | 11 | 13.57 | 9.7 | 15 | 13.17 | 12.6 | 15 | 12.77 | 15.5 | 18.5 | 12.47 | 18.3 | 22 | 12.17 | 21.2 | 30 | 11.87 | 24.1 | 30 | 11.57 | 27 | 37 | 11.37 | 29.9 | 37 | 4
| 1750 | 20.9 | 18.7 | 4.9 | 7.5 | 18.1 | 8.3 | 11 | 17.6 | 11.8 | 15 | 17.1 | 15.2 | 18.5 | 16.8 | 18.7 | 22 | 16.4 | 22.2 | 30 | 16.1 | 25.6 | 30 | 15.8 | 29.1 | 37 | 15.5 | 32.6 | 45 | 15.3 | 36 | 45 | 4
| 2000 | 23.8 | 21.62 | 5.6 | 7.5 | 21 | 9.5 | 15 | 20.52 | 13.5 | 18.5 | 20.12 | 17.4 | 22 | 19.72 | 21.4 | 30 | 19.42 | 25.3 | 30 | 19.12 | 29.3 | 37 | 18.82 | 33.2 | 45 | 18.52 | 37.2 | 45 | 18.32 | 41.2 | 55 | 2
| 2250 | 26.8 | 24.6 | 6.4 | 11 | 24 | 10.7 | 15 | 23.5 | 15.2 | 18.5 | 23.1 | 19.6 | 30 | 22.7 | 24.1 | 30 | 22.4 | 28.5 | 37 | 22.1 | 33 | 45 | 21.8 | 37.4 | 45 | 21.5 | 41.9 | 55 | 21.3 | 46.4 | 55 | 2
JAS-145 | 970Δ | 17.5 | 13.88 | 4 | 5.5 | 13.18 | 6.9 | 11 | 12.48 | 9.8 | 15 | 11.78 | 12.8 | 18.5 | 11.28 | 15.7 | 18.5 | 10.78 | 18.6 | 22 | 10.28 | 21.6 | 30 | 9.6 | 25.2 | 30 | [6 empty] | 6
| 1150 | 20.9 | 17.8 | 4.8 | 7.5 | 16.8 | 8.5 | 11 | 16.1 | 12.3 | 15 | 15.5 | 15.2 | 18.5 | 14.9 | 18.6 | 22 | 14.4 | 22.1 | 30 | 13.9 | 25.6 | 30 | 13.6 | 31.1 | 37 | 13.2 | 33.3 | 45 |  |  |  | 4
| 1450Δ | 26.3 | 22.8 | 6 | 7.5 | 21.9 | 10.5 | 15 | 21.2 | 15 | 18.5 | 20.5 | 19.5 | 30 | 20 | 24 | 30 | 19.5 | 28.5 | 37 | 19 | 33 | 37 | 18.6 | 37.6 | 45 | 18.2 | 41.2 | 55 |  |  |  | 4
| 1750 | 31.7 | 28.6 | 7.3 | 11 | 27.7 | 12.5 | 15 | 27 | 17.8 | 22 | 26.3 | 23.1 | 30 | 25.8 | 28.3 | 37 | 25.3 | 33.6 | 45 | 24.8 | 38.9 | 45 | 24.5 | 44.2 | 55 | 24.1 | 49.5 | 75 |  |  |  | 4
| 2000 | 36.2 | 33.2 | 8.3 | 11 | 32.3 | 14.3 | 18.5 | 31.6 | 20.3 | 30 | 30.9 | 26.3 | 37 | 30.3 | 32.4 | 45 | 29.9 | 38.4 | 45 | 29.4 | 44.4 | 55 | 29 | 50.5 | 75 | 28.6 | 56.6 | 75 |  |  |  | 2
| 2250 | 40.7 | 37.7 | 9.4 | 15 | 36.8 | 16.1 | 22 | 36.1 | 22.9 | 30 | 35.4 | 29.6 | 37 | 34.8 | 36.5 | 45 | 34.4 | 43.2 | 55 | 33.9 | 50 | 75 | 33.5 | 56.9 | 75 | [6 empty] | 2
JAS-150 | 970Δ | 21.6 | 17.6 | 4.9 | 7.5 | 16.5 | 8.5 | 11 | 15.6 | 12.1 | 15 | 14.9 | 15.7 | 18.5 | 14.2 | 19.3 | 30 | 13.6 | 22.9 | 30 | 13.1 | 26.5 | 30 | [9 empty] | 6
| 1150 | 25.6 | 22.1 | 5.7 | 7.5 | 21 | 9.9 | 15 | 20.1 | 14.2 | 18.5 | 19.4 | 18.5 | 22 | 18.7 | 22.8 | 30 | 18 | 27.1 | 37 | 17.5 | 31.4 | 37 | [9 empty] | 4
| 1450Δ | 32.3 | 28.3 | 7.2 | 11 | 27.2 | 12.6 | 18.5 | 26.3 | 18 | 22 | 25.6 | 23.4 | 30 | 24.9 | 28.8 | 37 | 24.3 | 34.2 | 45 | 23.8 | 39.6 | 45 | 23.3 | 45 | 55 | [6 empty] | 4
| 1750 | 38.9 | 35.4 | 8.7 | 15 | 34.3 | 15.2 | 18.5 | 33.4 | 21.7 | 30 | 32.7 | 28.2 | 37 | 32 | 34.7 | 45 | 31.4 | 41.2 | 55 | 30.9 | 47.8 | 55 | 30.4 | 54.4 | 75 | [6 empty] | 4
| 2000 | 44.5 | 41 | 10 | 15 | 39.9 | 17.4 | 22 | 39 | 24.8 | 30 | 38.3 | 33.3 | 45 | 37.6 | 39.7 | 45 | 37 | 47.2 | 55 | 36.4 | 54.7 | 75 | [9 empty] | 2
JAS系列三叶成组型罗茨鼓风机性能表 Performance Date of JAS Series Roots Blower 续表:table cont(1)
风机型号 | r/min n: 转速; m3/min Qth: 理论流量; 9.8kPa Qs: 各排气压力下的进口流量Qs(m3/min),所需轴功率La(kW)及所配电机功率Po(kW); Motor pole P: 电机
| Speed | Thero volume | Inlet volume Qs(m3/min) shaft power required La (kW) and motor power Po(kW) at each discharge pressure | [29 empty] | 极数
Type | r/min n: r/min; m3/min Qth: m3/min; 9.8kPa Qs: 9.8kPa; 19.6kPa Qs: 19.6kPa; 29.4kPa Qs: 29.4kPa; 39.2kPa Qs: 39.2kPa; 49.0kPa Qs: 49.0kPa; 58.8kPa Qs: 58.8kPa; 68.6kPa Qs: 68.6kPa; 78.4kPa Qs: 78.4kPa; 88.2kPa Qs: 88.2kPa; 98.0kPa Qs: 98.0kPa; Motor pole P: Motor pole
| n | Qth | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | Qs | La | Po | P
JAS-190 | 730Δ | 27.4 | 22.1 | 6.6 | 11 | 21.3 | 11.2 | 15 | 20.3 | 15.7 | 18.5 | 19.5 | 20.3 | 30 | 18.7 | 24.9 | 30 | 18.1 | 29.4 | 37 | 17.5 | 33.9 | 45 | 17 | 38.5 | 45 | 16.6 | 43.1 | 55 |  |  |  | 8
| 970Δ | 36.8 | 31.9 | 8.4 | 11 | 30.7 | 14.5 | 18.5 | 29.7 | 20.6 | 30 | 28.9 | 26.7 | 37 | 28.1 | 32.8 | 45 | 27.5 | 39 | 45 | 26.9 | 45.1 | 55 | 26.4 | 51 | 75 | 26 | 57.3 | 75 | 25.6 | 63.5 | 75 | 6
| 1170 | 44.5 | 40.1 | 10.2 | 15 | 38.9 | 17.6 | 22 | 37.9 | 25 | 30 | 37.1 | 32.4 | 45 | 36.3 | 39.8 | 45 | 35.7 | 47.1 | 55 | 35.1 | 54.7 | 75 | 34.6 | 62.1 | 75 | 34.2 | 69.5 | 90 | 33.8 | 77 | 90 | 4
| 1250 | 47.5 | 43.1 | 11.2 | 15 | 41.9 | 19 | 30 | 40.9 | 26.9 | 37 | 40.1 | 34.8 | 45 | 39.3 | 42.7 | 55 | 38.7 | 50.6 | 75 | 37.1 | 58.5 | 75 | 36.6 | 66.4 | 75 | 36.2 | 74.3 | 90 | 35.8 | 82.2 | 110 | 4
| 1350 | 51.4 | 47 | 12.2 | 18.5 | 45.8 | 20.6 | 30 | 44.8 | 29.1 | 37 | 44 | 37.6 | 45 | 43.2 | 46 | 55 | 42.6 | 54.5 | 75 | 42 | 63 | 75 | 41.5 | 71.4 | 90 | 41.1 | 79.9 | 90 | 40.7 | 88.4 | 110 | 4
| 1450Δ | 55.1 | 50.2 | 13 | 18.5 | 49 | 22.1 | 30 | 48 | 31.2 | 37 | 47.2 | 40.3 | 55 | 46.4 | 49.4 | 75 | 45.8 | 58.5 | 75 | 45.2 | 67.6 | 90 | 44.7 | 76.7 | 90 | 44.3 | 85.8 | 110 | 43.9 | 94.9 | 110 | 4
JAS-195 | 730Δ | 34.2 | 29.8 | 8.2 | 11 | 28.1195 | 13.9471 | 18.5 | 26.8108 | 19.7206 | 30 | 25.7031 | 25.4942 | 30 | 24.7313 | 31.2677 | 37 | 23.8544 | 37.0412 | 45 | 23.043 | 42.8148 | 55 | 22.2879 | 48.5883 | 55 | 21.5823 | 54.3619 | 75 | 20.9149 | 60.1354 | 75 | 8
| 970Δ | 46 | 41.8 | 10.9 | 15 | 40.0822 | 18.5324 | 30 | 38.7468 | 26.2041 | 30 | 37.6165 | 33.8758 | 45 | 36.6249 | 41.5475 | 55 | 35.73 | 49.2192 | 55 | 34.9021 | 56.8909 | 75 | 34.1315 | 64.5626 | 75 | 33.4116 | 72.2343 | 90 | 32.7306 | 79.906 | 90 | 6
| 1170 | 55.6 | 48.9 | 12.5 | 18.5 | 47.2002 | 21.3983 | 30 | 45.8648 | 30.2563 | 37 | 44.7345 | 39.1143 | 45 | 43.7429 | 47.9724 | 55 | 42.8481 | 56.8304 | 75 | 42.0201 | 65.6884 | 75 | 41.2496 | 74.5465 | 90 | 40.5296 | 83.4045 | 110 | 39.8486 | 92.2625 | 110 | 4
| 1250 | 59.4 | 56.1 | 14.2 | 18.5 | 54.3182 | 24.2641 | 30 | 52.9828 | 34.3085 | 45 | 51.8525 | 44.3529 | 55 | 50.8609 | 54.3972 | 75 | 49.9661 | 64.4416 | 75 | 49.1381 | 74.486 | 90 | 48.3676 | 84.5304 | 110 | 47.6476 | 94.5748 | 110 | 46.9666 | 104.6191 | 132 | 4
| 1350 | 64.2 | 59.9 | 15.1 | 18.5 | 58.1145 | 25.7925 | 37 | 56.7791 | 36.4696 | 45 | 55.6487 | 47.1467 | 55 | 54.6571 | 57.8238 | 75 | 53.7623 | 68.5009 | 90 | 52.9343 | 79.178 | 90 | 52.1638 | 89.8551 | 110 | 51.4439 | 100.5322 | 132 | 50.7629 | 111.2093 | 132 | 4
| 1450Δ | 68.9 | 64.6 | 16.2 | 22 | 62.8598 | 27.7031 | 37 | 61.5244 | 39.1711 | 45 | 60.3941 | 50.6391 | 75 | 59.4025 | 62.1071 | 75 | 58.5077 | 73.5751 | 90 | 57.6797 | 85.0431 | 110 | 56.9092 | 96.5111 | 110 | 56.1892 | 107.9791 | 132 | 55.5082 | 119.447 | 160 | 4
JAS-200 | 730Δ | 41.8 | 36.5 | 9.8 | 15 | 34.9 | 16.7 | 22 | 33.6 | 23.6 | 30 | 32.4 | 30.5 | 37 | 31.4 | 37.4 | 45 | 30.4 | 44.3 | 55 | 29.5 | 51.2 | 75 | 28.7 | 58.2 | 75 | 27.9 | 65.2 | 75 |  |  |  | 8
| 970Δ | 56.4 | 51.1 | 12.6 | 18.5 | 49.5 | 22 | 30 | 48.2 | 31.4 | 37 | 47 | 40.8 | 55 | 46 | 50.2 | 75 | 45 | 59.6 | 75 | 44.1 | 69 | 90 | 43.3 | 78.4 | 90 | 42.5 | 87.8 | 110 | 41.7 | 97.2 | 110 | 6
| 1170 | 68 | 62.7 | 15.3 | 22 | 61.1 | 26.5 | 37 | 59.8 | 37.8 | 45 | 58.6 | 49 | 75 | 57.6 | 60.3 | 75 | 56.6 | 71.5 | 90 | 55.7 | 82.8 | 110 | 54.9 | 94.1 | 110 | 54.1 | 105.4 | 132 |  |  |  | 4
| 1250 | 72.7 | 67.4 | 16.3 | 22 | 65.8 | 28.4 | 37 | 64.5 | 40.5 | 55 | 63.3 | 52.6 | 75 | 62.3 | 64.7 | 75 | 61.3 | 76.8 | 90 | 60.4 | 88.9 | 110 | 59.6 | 101.4 | 132 | 58.8 | 113.1 | 132 |  |  |  | 4
| 1350 | 78.4 | 73.1 | 17.3 | 30 | 71.5 | 30.2 | 45 | 70.2 | 43.2 | 55 | 69 | 56.1 | 75 | 68 | 69.1 | 90 | 67 | 82 | 110 | 66.1 | 95 | 110 | 65.3 | 108 | 132 | [6 empty] | 4
| 1450Δ | 84 | 78.8 | 18.6 | 30 | 77.2 | 32.6 | 45 | 75.9 | 46.7 | 55 | 74.7 | 60.7 | 75 | 73.7 | 74.8 | 90 | 72.7 | 88.8 | 110 | 71.8 | 103 | 132 | 71 | 117 | 132 | 70.2 | 131 | 160 | 69.4 | 145 | 160 | 4
JAS-250 | 730Δ | 53.2 | 46.7 | 11.7 | 15 | 44.7 | 20.6 | 30 | 42.9 | 29.5 | 37 | 41.4 | 38.4 | 45 | 40.1 | 47.3 | 55 | 38.9 | 56.2 | 75 | 37.7 | 65.5 | 75 | [9 empty] | 8
| 970Δ | 71.7 | 65.3 | 15.3 | 22 | 63.3 | 27.2 | 37 | 61.5 | 39.1 | 45 | 60 | 51.1 | 75 | 58.7 | 63 | 75 | 57.5 | 75 | 90 | 56.3 | 87 | 110 | [9 empty] | 6
| 1170 | 86.5 | 80 | 18.4 | 30 | 78 | 32.8 | 45 | 76.2 | 47.2 | 55 | 74.7 | 61.6 | 75 | 73.4 | 76 | 90 | 72.2 | 90.4 | 110 | 71 | 105 | 132 | [9 empty] | 4
| 1250 | 92.4 | 86 | 20.4 | 30 | 84 | 35.6 | 45 | 82.2 | 50.8 | 75 | 80.7 | 66.1 | 75 | 79.4 | 81.3 | 90 | 78.1 | 96.6 | 110 | 76.9 | 112 | 132 | [9 empty] | 4
| 1350 | 99.9 | 93.4 | 21.4 | 30 | 91.4 | 38.1 | 55 | 89.6 | 54.8 | 75 | 88.1 | 71.5 | 90 | 86.8 | 88.2 | 110 | 85.6 | 105 | 132 | [12 empty] | 4
| 1450Δ | 107.2 | 100.7 | 23.1 | 30 | 98.7 | 40.8 | 55 | 96.9 | 58.6 | 75 | 95.4 | 76.4 | 90 | 94.1 | 94.2 | 110 | 92.9 | 112 | 132 | 91.6 | 131 | 160 | [9 empty] | 4
注： 1：Δ所示转速的罗茨鼓风机为直联传动，其余为带联传动；
2：根据表中配套电机功率Po和电机极数P可在“电机额定输出功率数据表”中直接查取电机型号。
Note: 1：Δindicate the speed of Roots blowers which are direct coupling,the others are belt dirve。
2：Please search the motor type among "Date table for output rating of motor " allording to motor Power Po and motor pole P of matched motors listed in this table。